## Slide 1
Presented by Ronnie Mckenzie
Introduction

## Slide 2
Understanding
Leakage
By
Ronnie Mckenzie
2018

## Slide 4
Major transfers in South Africa
Major Interbasin Transfer Schemes in SA
Notes: Notes:
As a result of the skewed distribution of water resources and the high demands in the central interior of South Africa, many inter-basin transfers schemes have been developed.
Each arrow represents a transfer.
The purpose is to move water from areas of surplus to areas of deficit.
The transfer schemes are large and very expensive.
It is expected that upon completion, Phases 1a and 1b of the Lesotho Highlands Water Project will cost in excess of $ 3 billion (at today’s prices).

## Slide 5
Slide Courtesy Malose Ngoepe from DWS : Hydrology
Storage at 12 Oct 2016
16167 = 50%

## Slide 6: April 2019 Monitoring Report
6

## Slide 7: April 2019 Monitoring Report
7

## Slide 8: April 2019 Monitoring Report
8

## Slide 9: April 2019 Monitoring Report
9

## Slide 10: Vaal System Storages: June 2019

## Slide 11: Typical flow logging: 3 days
Flow

## Slide 12
Office Complex: 4 week logging showing no problems for whole month

## Slide 13
Initial Leakage
No Leakage
First small leak repair
Main leak repair
Normal Weekday demand
Normal Weekend demand
Office Complex: 10 week logging showing 80% reduction in water use as leaks repaired

## Slide 14
Office Complex: 4 week logging showing toilet cistern sticking

## Slide 15: Office Complex: 6 week logging showing leak developing and repair

## Slide 17: 1: Typical flow and pressure logging
Flow
Pressure

## Slide 19
Minimum Day Flow: A new Concept ???

## Slide 21: Origins of Models
Based on ARSP Model from Canada – 1983
Prof Loucks – Cornell
Prof Stedinger – Cornell
Prof Grieg – Colorado State
Resource Software design originally in FORTRAN
Stochastic Software by Prof Pegram : University of Natal.

## Slide 22
A mock-up of how scientists thought a home computer would look in the year 2004 as suggested by the RAND Corporation in 1954

## Slide 23: VAX 780 (1983)

## Slide 24
Creating a System Model

## Slide 25: Typical simple water resource system

## Slide 26: Initial System Model

## Slide 27: Penalty Structures Added

## Slide 28: Internal Node and arc network (storage reservoirs converted to flow arcs allowing each time interval to be solved using an “Out of Kilter” LP solver)

## Slide 29
Thank You
Integrated Orange /Vaal system

## Slide 31: Orange/Senqu Water Resource System
87 Large Dams
279 Small Dams
± 1 250 Abstractions/Demand Centres
8 integrated subsystems
± 4 000 channels/arcs
Over 300 naturalized streamflow records
Over 300 point rainfall time series

## Slide 32
Naturalization of Hydrology

## Slide 33: Naturalization of Streamflow Data

## Slide 34: Streamflow Record at Current Development Levels

## Slide 35: Streamflow Record at Current Development Levels

## Slide 36
Use of Stochastic Hydrology

## Slide 37
Projected system volume trajectories

## Slide 38
Results for sequences
Min % 5.0 % 25 % 50 % 75 % 95 % Max %
Percentage of sequence results exceeding given value

## Slide 39
Projected system volume trajectories

## Slide 40
Projected system volume trajectories

## Slide 41
Historical
reservoir levels
Levels below which
curtailments are imposed
Restrictions
imposed
Restrictions
lifted

## Slide 42: Vaal System Storage at April 2019
42
Slide Courtesy DWS AOA

## Slide 43: Grootdraai Dam
43
Slide Courtesy DWS AOA

## Slide 44: Sterkfontein Dam
44
Slide Courtesy DWS AOA

## Slide 45: Main Lesotho Reservoirs
45

## Slide 48
n = 0.030

## Slide 49
n = 0.040

## Slide 50
n = 0.050

## Slide 51
n = 0.060

## Slide 52
n = 0.070

## Slide 53: How much water is lost from a leak ?
Leakage rates for various mains bursts ??? |  |  |  |  | 
Pipe | System | Leakage Rate |  | Leakage | Water
Diameter | Pressure |  |  | Duration | Lost
mm | m | m3/s | m3/hr | Hours | m3
100 | 50 | 0.2459 | 885 | 2.00 | 1770
100 | 80 | 0.3110 | 1120 | 1.58 | 1769
150 | 60 | 0.6060 | 2182 | 2.48 | 5410
150 | 70 | 0.6546 | 2356 | 1.04 | 2451
100 | 90 | 0.3299 | 1188 | 1.79 | 2126
100 | 90 | 0.3299 | 1188 | 1.41 | 1675
100 | 80 | 0.3110 | 1120 | 1.20 | 1344
100 | 90 | 0.3299 | 1188 | 2.09 | 2482
150 | 30 | 0.4285 | 1543 | 5.15 | 7944
250 | 60 | 1.6833 | 6060 | 2.00 | 12120
 |  |  |  |  | 39091

## Slide 54: Typical burst flow rates at 50m pressure

## Slide 55
200 m3/hr for 3 hours = 600 m3

## Slide 56
40 m3/hr for 6 hours = 240 m3

## Slide 57
20 m3/hr for 3 hours = 60 m3

## Slide 58
1 m3/hr for 3 months = 2 232 m3

## Slide 59
Sprinkler at approximately 1 m3/hr
Notes: 59

## Slide 60
0.5 m3/hr for 3 years = 13 140 m3

## Slide 61
Photos: Courtesy Caryn Seago

## Slide 62
Photo: Courtesy Tim Waldron

## Slide 63
Photo: Courtesy Trevor Westman

## Slide 65: How much water is used in a household ?

## Slide 66
Dual Water
meter

## Slide 67
42 m3 over 3 months
= 14 m3 /month @ R5/m3
= ± R70/month
619 m3 over 3 months
= ± 200 m3 /month @ R5/m3
= ± R1000/month

## Slide 68
Leaking tap at approximately 250 litres/hr (200 m3/month)

## Slide 69
Leaking hose at toilet cistern of approximately 100 litres/hr

## Slide 70
Low income area – No Payment for water
Average water use of > 60 m3/month

## Slide 71
High income area – full payment for water
Average use ± 15 m3/month if no pool or irrigation

## Slide 72: Catastrophic Failure of 600mm Bulk Main

## Slide 73
20 m3/hr

## Slide 74
20 m3/hr = MMMI of 1/month
(The Mike Mercedes Index: Courtesy Prof. Mike Muller)
In 1 month

## Slide 75
20 m3/hr = MMMI of 12/year
(The Mike Muller Mercedes Index: Courtesy Prof. Mike Muller)
In 1 year

## Slide 76: Some background to Water Loss Management in South Africa

## Slide 77
4 WRC
MODELS

## Slide 79: Night Flow Analysis

## Slide 80
Analysis of minimum night flow logging results from SANFLOW
First of the BABE Models to incorporate error sensitivity

## Slide 81
Interpretation of MNF
Notes: Notes:
In order to establish if a zone has leakage problems it is necessary to split the MNF into its various components:
  Burst leakage;
  Background leakage;
  Legitimate night use.
The burst and background leakage are then spilt into three components that are measured or estimated using standard figures:
  Mains leakage;
  Connection pipe leakage;
  Property leakage.
The components of background leakage are estimated using:
  Length of mains;
  Number of connections;
  Some basic leakage parameters selected to suit the particular system being analysed.
The legitimate night use is estimated from the population, toilet cistern size and information on any large users, etc.
Having calculated or estimated the background leakage and legitimate night use, the burst leakage can then be established as the difference between the MNF and the sum of the legitimate use and background leakage

## Slide 82: Pressure Management

## Slide 83: Low Pressure
Photo: Courtesy Ken Brothers

## Slide 84
High Pressure
Photo: Courtesy Ken Brothers

## Slide 88
Estimated Damage = ± $15 million

## Slide 89
Analysis of pressure logging results can be undertaken using PRESMAC
Assessment of potential savings from various forms of advanced pressure control

## Slide 90
Pressure Analysis

## Slide 94
© WRP (Pty) Ltd, 2001

## Slide 95
Khayelitsha : 2000

## Slide 96
Khayelitsha
± 70 000 stands
± 110 000 households
Average pressure 60m to 80m
Over 450 000 residents

## Slide 98
Photo Courtesy Tertius de Jager

## Slide 99: Hourly: Savings = 1000 m3/hr
Olympic swimming pool every 2 hours

## Slide 100
Sebokeng : 2005

## Slide 101
Direction of Flow
From Rand Water
Direction of Flow
From Rand Water
High Pressure from Rand Water
Lower Pressure to Sebokeng & Evaton
During off-peak periods
Direction of Flow
From Rand Water
Direction of Flow
From Rand Water
Direction of Flow
To Sebokeng
Direction of Flow
To Evaton

## Slide 103
Photo courtesy Technolog

## Slide 104: Sebokeng Savings
Saving ± 10 million m3 per annum (± 27 Ml/day)

## Slide 105
Mitchells Plain : 2009
Photo Courtesy Tertius de Jager of CoCT

## Slide 106: Details for 1220 mm Ø PRV Chamber

## Slide 107
Photo courtesy Technolog

## Slide 108: Water Balance

## Slide 109
First Excel based Water Balance Model based on the Standard IWA Water Balance Methodology

## Slide 110
Modified IWA Water Balance to Allow for Free Basic Water Component in SA

## Slide 111: Economics of Leak Location

## Slide 112
Assessment of the most appropriate level of Active Leakage Control based on BABE Principles

## Slide 113: What about Leakage ? New Technology – High Tech

## Slide 114
Leak Location by Satellite
( 300% increase in satellites by 2024)

## Slide 116
Leaking Connection on Narmada pipeline

## Slide 117: What about Leakage ? New Technology – Low Tech

## Slide 119
Large Canine Leak Detector(LCLD) for Mains Leaks
Photo: Courtesy United Utilities

## Slide 120
Small Canine Leak Detector (SCLD) for Connection Leaks

## Slide 123: Continuous Monitoring

## Slide 125: Some Logging Results

## Slide 126: 2 : Interpretation of flow logging
● Stable domestic flow pattern – main peak in morning
● Average daily flow = ± 150 m3/hr
● MNF/ADD = ± 53% indicating possible leakage problem
● Minimum night flow = ± 80 m3/hr

## Slide 127
Leak running at ± 1.6 m3/hr for 10 days
Cost of leak
± 10 * 24 * 1.6 * 20
= ±R8 000 in 10 days
Leak develops
Leak repair
Leakage

## Slide 128: Industry 2 Leak – Before and After

## Slide 129: Leak Repaired at Townhouse Complex

## Slide 132
Before
After

## Slide 133
Average water use 41 m3/hr
Average water use 16 m3/hr

## Slide 134: Intermittent Supply : Don’t go there !
Average Flow = 17.4 m3/hr
Average Flow = 14.0 m3/hr

## Slide 135: Office Park - Flow

## Slide 136: Growing leak at office complex

## Slide 137: Leak identification and repair at Office Park

## Slide 138: Intermittent Supply

## Slide 139
Mixture of Sewage
& Potable Water

## Slide 140
Intermittent Supply
● MNF = ± 165 m3/hr
● No supply during night
● rapid refilling of empty pipes
● MNF/ADD = ± 83%
● ADD = ± 200 m3/hr
Flow

## Slide 141
Initial Avg Flow : 135 m3/hr

## Slide 142
Initial Avg Flow : 135 m3/hr
Reduced Avg Flow : 95 m3/hr

## Slide 143: Comments from Bambos Charalambous (IWA: Bangalore 2016)
Intermittent supply is not an appropriate response to drought or water shortage
It takes 1 hour to switch to intermittent supply but 2 years to return to 24/7 (at great cost)

## Slide 144: Recommendations
Try everything else before introducing intermittent supply
Intermittent supply is the measure of last resort
Rather reduce water pressure but try to maintain 24/7
Take action early on in a drought
Take action now to reduce wastage

## Slide 145
Climate Change
What is happening and what impact will it have on water resources ?

## Slide 149
Climate Change
Clear evidence that the climate is changing.
Difficult to quantify or predict the influence of future Climate Change on rainfall and streamflow
What is the impact of land use change relative to Climate Change ?
Christiana Figueres (Sky News 28 October 2015) “ Natural disasters are not caused by Climate Change but the intensity and frequency of such disasters are exacerbated by Climate Change”

## Slide 150
Example calculation of CO2 savings

## Slide 151
Solar Panels Installed at an Embassy in Pretoria

## Slide 152
Cost of the Panels ± R8 mil (± $1 mil)

## Slide 153
Panels Save ± 90 Tonnes CO2 Per Annum

## Slide 154: Pressure Management v Embassy Solar Panels
Pressure Management
Capital Cost R5 mil ($650 k)
Saves 13 000 tonnes CO2/yr
Value of CO2 = R2.1 mil/a
Water savings R30 mil/a
Interest R500 000/a
Payback less than 3 months
Solar Panels at Embassy
Capital Cost R8 mil ($1 mil)
Saves 90 tonnes CO2/yr
Value of CO2 = R18 000
Electricity savings R300 000/a
Interest R800 000/a
Payback NEVER !!
Note: The figures are for this specific example and figures may vary from case to case

## Slide 155: Enhancing Water Security
Water Resource Management: Priorities
Continue to plan using risk based approach
Agree on acceptable risks for each demand
Implement restrictions early in drought cycle
Facilitate water market.

## Slide 156
Water Use Efficiency: Priorities
Repair reported leaks quickly
Reduce pressure (pressure creates leakage)
Use Tariffs to curtail demand in emergencies
Change behaviour on water use
Do not introduce intermittent supply
Consider leakage as cheapest new resource

## Slide 157: THE END